Boiler Treating

Before installation of boiler, the contractor shall recirculate 500 ml Fernox F3 System Cleaner or 1.5% mixture by volume, combined with plain water.  Recirculation shall occur for a period of 3 hours up to 1 week, at contractor’s discretion, dependant on system age.  Fernox Cleaner F3 shall be circulated at normal heating mode operating temperature.

After recirculation, system shall be strategically flushed of all debris.  Drainage and flushing shall occur a minimum of two times, using plain water, until water runs clear.  In the case that a powerflushing unit is being used, cleaning should be completed in no longer than an hour.

After new boiler is installed, system shall be filled with Fernox Protector F1 at 1-2% fluid by volume.  Any other Fernox products required shall be installed as per manufacturers specifications.

All Fernox products shall be purchased through an authorized Fernox stocking wholesaler, as per classification by Klimatrol.