RADIANT FLOOR HEATING SYSTEM

Furnish a REHAU Radiant Floor Heating system as prepared and supplied by KLIMATROL Environmental Systems Ltd. (Tel.: 905-454-1742). c/w RAUPEX piping, distribution manifolds, REHAU “Everloc” type embeddable tubing couplings (if required), Thermostats or Floor Temperature Controllers, Indoor Outdoor Temperature Reset Mixing valve Controls system, supply and return sensors, ambient temperature sensor,  4-Way mixing valve, actuator, pressure and temperature gauges, system pump and floor heat installation specialities as required for the complete system.  Equipment, detailed pipe layout shop drawings, technical support and any field contractor supervision shall be provided by Klimatrol. REHAU 25 Year warranty shall be applicable to this installation. Installing mechanical contractor shall have previous experience with the installation of hydronic slab heating systems. References must be provided.

The floor heating component manufacturer, REHAU, shall warrant the cross-linked polyethylene tubing and all related water distribution components, except controls, to be free from defects in material and workmanship for a period of twenty-five (25) years.

Material:  All tubing shall be high density cross-linked polyethylene as manufactured by REHAU. Tubing shall have a co extruded oxygen diffusion barrier.

Only “EVERLOC” permanent brass fittings utilizing REHAU proprietary compression technology shall be approved for installation within the thermal mass.

Manifolds shall be brass and equipped with isolation and balancing valves for each circuit.

Manifold Security covers (if required) shall be provided by installing contractor.

The control and sensors shall be capable of automatically operating the system including: indoor outdoor reset control set-point, summer shutdown on outdoor temperature rise, modulating the temperature input into slab, remote enable/disable switch.

Complete a pressure test of the system prior to installing thermal mass with either air or water (take necessary precautions to prevent water from freezing).

Complete all inspection and test reports as supplied by the manufacturer of the system.