## 1		GENERAL

1.1		General

.1	Conform to Sections of Division 1 as applicable.

.2	Conform to Mechanical General Requirements Section 15010 as applicable.

  - References

.1	ASTM F 876: Standard Specification for Cross-linked Polyethylene (PEX) Pipe

.2	ASTM F 877: Cross-linked Polyethylene (PEX) Plastic Hot- and Cold-Water Distribution Systems

.3	ASTM F 2080: Standard Specification for Cold-Expansion Fittings with Metal Compression-Sleeves for use with Cross-linked Polyethylene (PEX) Pipe

.4	CSA B 137.5: Cross-linked Polyethylene (PEX) Tubing Systems for Pressure Applications

.5	DIN 4726: German Standard for Plastic Piping Used in Warm Water Floor Heating Systems

1.3		Submittals

.1	Provide submittals and shop drawings in accordance with the General Requirements and as specified herein.  Submit shop drawings indicating schematic layout of system, including equipment, critical dimensions and piping/slab penetration details as well as details for protecting exposed PEX piping.

.2	Submit manufacturer's technical installation instructions.

.3	Submit independent certification results for the piping systems from a recognized testing laboratory.

.4	Submit computer-generated RFH system design indicating pipe sizing and panel performance at pipe spacing and water temperatures selected.  RFH design calculations to be performed on pipe manufacturer’s software.

.5	Submit catalog data on all equipment, fittings, fasteners and associated items necessary for the installation of the piping and manifolds.

.6	Systems shall be installed by a contractor experienced in radiant floor cooling / heating system pipe installation. Submit installer’s installation certification and project installation resume of experience.

.7	Manufacturers shall provide owner with a 25 Year warranty on pipe and Everloc fitting system.

1.4		Work Included

.1	Descriptions:  Furnish and install a radiant floor heating (RFH) system.  Systems shall be complete with Rehau piping, distribution manifold(s) with circuit balancing valves, sleeves for slab sensors, manifold zone valves or circuit actuators, temperature mixing valves, manufacturer-approved cold-expansion compression-sleeve pipe repair couplings, non-metallic pipe fasteners, installation accessories, installation supervision and field engineering as required for a complete and proper functioning system.

1.5		Regulatory Requirements

.1	Cross-linked polyethylene (PEXa) pipe shall be manufactured by the high-pressure peroxide (Engel) method with a minimum degree of cross-linking of 80%, and conform to ASTM F 876, F 877 and CSA B 137.5.  Fittings shall conform to ASTM F 877, F 2080 and CSA B 137.5.  Pipe oxygen diffusion barrier shall conform to DIN 4726.

1.6		Delivery, Storage And Handling

1.	Deliver and store piping and equipment in shipping containers with labeling in place.  Pipe to be kept in original shipping boxes until required for installation.  Do not expose pipe to ultraviolet (sunlight) light for more than 90 days.

2.	Protect piping and manifolds from entry of contaminating materials by installing suitable plugs in all open pipe ends until installation.  Where possible, connect pipes to assembled manifolds to eliminate possibility of contaminants.

3.	Piping shall not be dragged across the ground or concrete surfaces, and shall be stored on a flat surface with no sharp edges.

4.	Pipe shall be protected from oil, grease, paint, direct sunlight and other elements as recommended by manufacturer.

## 2 	PRODUCTS

2.1		Piping

1.	Material:  All radiant floor heating piping shall be nominal high density cross-linked polyethylene using the peroxide method of cross-linking (PEXa) and with an approved cell classification in accordance with ASTM D 3350.  Pipe shall conform with ASTM F 876 and CSA B 137.5, and be certified by CSA or equivalent testing organization.

2.	Temperature and Pressure Ratings: Piping shall be rated for 100 PSIG gauge pressure at 180oF temperature (690 kPa @ 82°C) continuous, and 80 PSIG gauge pressure at 200oF temperature (550 kPa @ 93°C) continuous.

3.	Oxygen Diffusion Barrier: Piping shall have a co-extruded oxygen diffusion barrier capable of limiting oxygen diffusion through the pipe to less than 0.10 mg/l/day at 104oF (40°C) water temperature, in accordance with DIN 4726.

4.	Bend Radius: The minimum bend radius for cold bending of the pipe shall be not less than five (5) times the outside diameter.  Bends with a radius less than this shall require the use of a bending template as supplied by the pipe manufacturer, and/or hot air.

5.	All floor  heating piping shall be fastened using nylon cable binders to a middle rebar mesh (provided by general contractor) maintaining minimum 32 mm pipe clearance from top and bottom of the concrete slab and keeping the pipe centered in the concrete slab.

6.	If Raupex floor heat system is to be installed on an existing structural slab within a 40 – 70mm cement topping then Klimatrol shall provide 25mm railfix tube track for fastening Raupex pipe down.

2.3		Fittings

1.	Fittings shall be manufactured of dezincification-resistant brass and shall be supplied by the piping manufacturer as part of a proven cataloged system.  Manifold fittings to be compression nut style with split compression ring.

2.	Fittings shall be certified to ASTM F 877, F 2080 and CSA B 137.5 as part of the manufacturer’s PEX piping system.  Pipe couplings embedded within the thermal mass shall be EVERLOC® cold-expansion compression-sleeve fittings. Fittings shall carry a manufacturer’s 25 year warranty for installations in concrete.

2.4		Manifolds

1.	Material: Distribution manifolds shall be manufactured of brass and be supplied by the piping 			manufacturer as a proven cataloged part of the manufacturer's system.

2.	Balancing Manifolds: Brass balancing manifolds shall be equipped with visual flow gauges, balancing and isolation valves for each circuit, header isolation valves and air vent/fill ports.  Manifolds shall be pre-assembled, mounted on metal brackets and ready to install.

3.	Each manifold shall be provided with automatic air vents.

4.	Provide manifold cabinets of sufficient size to allow controls and manifold zone valves to be installed within the cabinet

2.5		Controls

1.	Slab Sensors shall be supplied by BMS Contractor unless otherwise specified or agreed.  Provide sleeves for installing 2 x temperature sensors per zone.  Coordinate with BMS Contractor.

2.	Valves and Actuators: Normally closed 24V 2-Way control valves for each manifold or circuit actuators for each loop shall be installed and on a call for heat allow fluid circulation through the slab heating system to maintain thermal zone setpoint.  Valves and/or circuit actuators shall be supplied by Klimatrol.

3.	Floor Heat thermostats shall be positioned as per mechanical drawings. Slab sensors shall provide high and low floor temperature limits.

2.6		Accessories

1.	Utilize manufacturer’s system installation accessories including: nylon cable binders, pipe sleeves, protective sleeving, pipe cutters, pipe uncoilers and other installation tools and aids pipe ties.

2.7		Performance

1.	As per schedule on drawings

Acceptable Manufacturer:

- Rehau

Alternate:

- Uponor

3	EXECUTION

3.1		Preparation

- Concrete Slab on Grade: Subgrade should be compacted, flat and smooth to prevent damage to pipe or insulation.  Approved vapor barrier material should be installed.  Insulation should be installed vertically along all exterior walls or footings to which the edge of the slab will meet against.  Horizontal insulation should be installed flat against the vapor barrier under where the slab will be poured.  Rigid foam board insulation panels should be taped together at the seams.  Reinforcing wire mesh or rebar, if required by structural design, must be flat and level, with all sharp ends pointing down.  Finished grade of the thermal mass must be a minimum of 3/4” (19 mm) above the top of PEX heating pipes.

- All floor  heating piping shall be fastened using nylon cable binders to a middle rebar mesh (provided by general contractor) maintaining minimum 32 mm pipe clearance from top and bottom of the concrete slab and keeping the pipe centered in the concrete slab.

- If Raupex floor heat system is to be installed on an existing structural slab within a 40 – 70mm cement topping then Klimatrol shall provide 25mm railfix tube track for fastening Raupex pipe down.

- Floor heat circuits shall be designed for maximum comfort and energy savings using a maximum 20 degree F. (11 deg.C) temperature difference and 125 deg.f. (52 deg.C) mean heating water temperature.

- Klimatrol shall provide shop drawing layout to minimize pipes crossing construction joints maintaining “thermal bays” to accommodate floor expansion and contraction. Floor covering shall be the same throughout each “Thermal bay”. Floor heating design consider the floor surface coverings.

- Floor heat system shall be installed in a counterflow spiral pattern as much as possible for even surface temperatures.

- Prior to thermal mass installation Mechanical Contractor shall be responsible for

  - neat professional installation of floor heating loops maintaining specified pipe spacing, labeling each circuit as well as loop lengths and recording an “as built” loop layout

  - using the manifold pressure test the system with air 68 psig and have pressure test witnessed by the General Contractor. Maintain pressure test until system is put into operation.

  - inspect the entire system for kinks or damage.

  - Complete a Klimatrol Floor Heat Installation Site Inspection report for each pour.

  - post job signs and advise other trades where the floor heating system is installed so they do not accidentally drill into system. Maintain system pressure test through out construction period.

  - Upon commissioning provide the owner with a “system asbuilt drawing” and manufacturer’s warranty for the floor heat system

  - Mechanical contractor shall not be responsible for wire mesh or insulation. These items shall be supplied and installed by the General Contractor.

  - General contractor shall discuss with the mechanical contractor the concrete pour pattern and shall strive to accommodate the floor heating layout.

3.	Pre-cast Concrete Subfloor: Subfloor must be clean and free from all construction debris, which could potentially damage the pipe.  Replace any areas that appear weak.  If called for by design, approved vapor barrier material should be installed and insulation should be installed vertically along all exterior walls or footings to which the edge of the slab will meet against, as well as flat against the vapor barrier under where the slab will be poured.  Rigid foam board insulation panels should be taped together at the seams.  Finished grade of the thermal mass over-pour must be a minimum of 3/4” (19 mm) above the top of PEX heating pipes.

3.2		Installation

.1	Install in accordance with manufacturer's published installation manual and/or published guidelines.

.2	Mount manifolds in the locations previously prepared or in previously installed cabinets, if used.  Manifolds should be mounted as level as possible.

.3	Route piping in orderly manner, according to layout and spacing shown in approved submittal drawings.  All notes on drawings shall be followed.

.4	At connections and fittings, use a plastic pipe cutter to ensure square and clean cuts, and join pipes immediately or cap ends of pipe to seal from contaminants. Where fittings are installed within the thermal mass, they shall be wrapped in chloride-free tape or sealed within a heat-shrink material approved by the manufacturer.

.6	Pipe should be dispensed using a suitable uncoiling device.  Remove all twists prior to securing pipe.  Pipe must lie flat on an even plane.  Finished grade of a thermal mass must be a minimum of 3/4” (19 mm) above the top of PEX heating pipes.  Fasten piping at no more than 3 feet (90 cm) intervals, being careful not to twist the pipe.  In thin concrete slabs, it may be necessary to secure piping every 2 feet (60 cm).  Use only fasteners supplied or approved by the manufacturer of the PEX pipe.

.7	Piping that must pass through expansion joints shall be covered in protective polyethylene convoluted sleeving (flexible conduit) extending 15 inches (38 cm) on each side of the joint.  Sleeving must be secured on pipe to prevent movement during installation of thermal mass.

.8	Where piping exits the thermal mass, a protective conduit shall be placed around the pipe, with the conduit extending a minimum of 6 inches (15 cm) into the floor and exiting by a minimum of 6 inches.  For penetrations at manifolds, use rigid PVC bend guides secured in place to prevent movement.

.9	At the time of installation of each circuit of pipe, connect the pipe to the correct manifold outlet and record pipe length for balancing.  If manifold is not installed, cap the end of the pipe and label the pipe's circuit numbers along with S for supply and R for return.  Connect pipes to manifold as soon as possible and record circuit lengths.  All circuits shall be labeled to indicate circuit length and serviced area.

.10	The following precautions shall be taken in areas intended for carpet:

1.	Notify carpet installer that radiant heating pipes have been installed.

2.	Keep pipes 6 inches (15 cm) from all wall baseplates.

3.	Install metal guards where pipe will pass through wall baseplates and where carpet tack strips will be installed.

.11	The following precautions shall be taken in areas intended for hardwood flooring:

1.	Ensure that nailing areas for hardwood flooring (if nailing is required) are clearly marked and known to hardwood installers.

.12	The heating system should not be put into operation until the poured concrete thermal mass has cured a minimum of 28 days, unless otherwise specified and approved by thermal mass supplier.  If it is necessary to operate the heating system to prevent freezing, a maximum flow temperature of 72o F (22°C) must not be exceeded while the thermal mass is curing.  After curing, gradually increase the flow temperature by no more than 10oF (6°C) each day until system reaches the required operating temperature.

.13	Contractor shall be responsible for provision of

1.	Wire mesh or rebar to secure tubing and any insulations to be provided by the general contractor

2.	Labour to install Radiant Floor Heating system

3.	Water, glycol and any chemical solutions.

4.	Field coordination of the pressure test equipment. (It is recommended to use the REHAU hydraulic pressure test unit available through Klimatrol to conduct pressure tests.)

5.	Supervision of concrete pours to instruct concrete installers on maintenance of pipe integrity and position of pipe in slab during concrete installation.

6.	Installation of control valves, pumps, supply and return piping, temperature sensors in sleeves, all valves and fittings.

7.	Electrical control interconnection and testing.

3.3		Field Quality Control

.1	Filling, Testing & Balancing: Tests of hydronic heating systems shall comply with local codes, and, where required, shall be witnessed by the building official. (Reference BOCA, ICBO, SBCCI or the acceptable code body for the jurisdiction).

1.	Pressure gauges used must show pressure increments of 1 PSIG and should be located at or near the lowest points in the distribution system.

.2	Air Test: Charge the completed, yet unconcealed pipes with air.  Do not exceed 150 PSIG.  Use liquid gas detector or soap solution to check for leakage at manifold connections.

1.	Perform a preliminary pressure test pressurizing the system to the greater of 1.5 times the maximum operating pressure or 100 psi for 30 minutes.  As the piping expands, restore pressure, first at 10 minutes into the test and again at 20 minutes.  At the end of the 30 minute preliminary test, pressure must not fall by more than 5 PSIG from the maximum, and there shall be no leakage.

2.	After performing the preliminary test, perform the main pressure test immediately.  The main pressure test shall last 2 hours.  The test pressure should be restored and must not fall more than 3 psig after 2 hours.  No leakage should be detected.

3.	Pressure shall be maintained and monitored during installation of the thermal mass.  If any leak is detected during installation of thermal mass, the leak must be found immediately and the area cleared for repair using manufacturer approved repair coupling.  Retest before covering repair.

.3	Water Test: Purge all air from pipes.  Charge the completed, yet unconcealed pipes with water. Take necessary precautions to prevent water from freezing. Check the system for leaks, especially at all pipe joints.

1.	Perform the same procedures as used in the Air Test (3.3.2.1 –3.3.2.3.).

3.4		Warranty

1.	The radiant floor heating pipe manufacturer shall warrant the cross-linked polyethylene piping to be free from defects in material and workmanship for a period of twenty-five (25) years.  The design shall be approved either by submittal or stamped by a registered engineer as being complete and accurate.

2.	All manifolds and controls shall be warranted for 18 months and/or two heating seasons.

END OF SECTION