Toronto North Collegiate Model- 9in

# Material Properties

| Material | Color | K-Value (BTUh/in F) |
| --- | --- | --- |
| Concrete | Gray | 0.045 |
| Tile (1/2”) | Red | 0.0139 |
| RAUPEX (5/8”) | Brown | 0.02 |

Go to next page for results and heat distribution.

Heat Distribution

Additional Conditions:

5/8” RAUPEX  9 in OC

HEATING-Top / Bottom Air Temp : 72F

COOLING- Top = 75F , Bottom = 79F

Film Coefficient: 1.65 (BTUh/ ft2 oF), Still Air on the top and bottom of the model

There are no additional conditions applied to the model

With these conditions and the material properties listed the following results were obtained

| MWT (F) | Output Floor (BTU / ft2) | Output Ceiling (BTU / ft2) | Surface Temp Floor (F) | Surface Temp Ceiling (F) | Pipe Location |
| --- | --- | --- | --- | --- | --- |
| 62 | 6.5 | 7.5 | 70-71 | 74-75 | 1.5” From Floor |
| 62 | 5 | 9.4 | 71-73 | 72-74 | Middle |
| 62 | 3.8 | 12.2 | 72-73 | 70-73 | 1.5” From Ceiling |
| 105 | 18 | 13 | 80-85 | 79-80 | 1.5” From Floor |
| 105 | 14.3 | 17.3 | 80-81 | 81-83 | Middle |
| 105 | 11 | 22.5 | 78-79 | 82-88 | 1.5” From Ceiling |