AIR COOLED MODULAR CHILLER

PART 1		GENERAL

- WORK INCLUDED

  - Work Included: The air-cooled modular chiller system shall consist of individual chiller modules that are assembled on site.  Each chiller module shall be completely factory wired, and tested prior to shipment.  Each module shall include a compressor, evaporator, air-cooled condenser, and controls. Controls shall be designed to allow the master controller to operate remaining slave modules in the event of a malfunction of any slave controller. The controls shall also be designed to operate on a distributed master control system which allows each individual slave microprocessor to operate on its own temperature sensor if there is a failure of the system temperature sensors.

  - Related Work Specified Elsewhere: General Requirements of Division One and Section 15010 “Basic Mechanical Requirements” pertain to and are hereby made part of the work of this Section of the specifications.

- QUALITY ASSURANCE

  - Unit shall be constructed in accordance with the UL 1995 and NEC standards and be UL or ETL listed.

  - Unit shall be rated and tested in accordance with ARI 550/590 – Standard for Water Chilling Packages.

  - Unit shall meet the safety standards of ANSI/ASHRAE 15 – Safety Standard for Refrigerated Systems.

- SUBMITTALS

  - Submit complete drawings including cabinet dimensional details and anchor point locations, required clearances, location and sizes of field connections, performance data, electrical wiring diagrams, dry and operation weights, and all required electrical data.

  - Submit manufacturer’s installation instructions, including any remote panel installation instructions.

  - Operating and Maintenance manuals: provide two copies of current commercial manuals.

  - DELIVERY, STORAGE, AND HANDLING

- Comply with manufacturer’s installation instructions for rigging, unloading, and transporting units.

- Protect units on site from physical damage after unloading.

- WARRANTY

  - Entire unit:  one year parts.  Compressor:  five years parts.

PART 2	PRODUCTS

- ACCEPTABLE MANUFACTURERS

  - ArctiChill

- CHILLER

  - General:  Each module shall be assembled on an integral epoxy coated welded channel steel frame and be enclosed with epoxy painted aluminum panels. The unit shall be shipped as individual modules and assembled on site.  Each module shall be fully charged with refrigerant and factory tested for capacity and controller functions prior to shipment.  Unit must be built for single point power supply connection to a central distribution block. The electrical distribution panel shall incorporate circuit breaker to provide branch circuit overload protection and electrical isolation for each chiller module. Electrical supply to each module shall consist of flexible conduit. No electrical connection to a module shall carry the load of more than that module. The electrical supply connections for each module shall be factory assembled and shipped with each module for field connection into the electrical distribution panel.

  - Frame:  Frame shall be constructed of welded structural channel steel and be epoxy powder coated with an oven baked finish.

  - Cabinet:  Epoxy coated aluminum panels on welded steel frame.  The cabinet enclosure shall include easily removable access panels for service.  Access panels shall be removable via stainless steel fasteners and retaining clips. Unit shall not require access via sheet metal screws or protruding threaded fasteners.

  - Compressors:  Hermetically sealed scroll compressors with rotalock connections, crankcase heaters, oil level sight glasses, suction gas-cooled motor with solid-state sensors in the windings for overload protection, and in-line fusing.  There shall be two, independent compressors and refrigerant circuits per module.  Compressors shall be mounted to the heavy gauge steel frame with rubber-in-shear isolators.

  - Evaporators:  Dual circuit, brazed plate evaporators constructed of 316 stainless steel plates and copper brazing.  The supply and return water piping connections to each evaporator shall include manual isolation valves to allow servicing of each module individually, while the remaining modules continue to operate.   The water connections to each evaporator shall utilize rolled groove couplings for service convenience and ease of installation.  Evaporators shall be insulated with ¾” closed cell insulation.  The minimum working pressure shall be 360 psi.  Evaporator piping fluid velocity shall not exceed 4 fps for pipe sizes 2” and smaller, or 7 fps at any point in the system, per ASHRAE Fundamentals Handbook.

  - Electronic control valves:  Each chiller module shall include an electronic isolation valve that allows system flow to the active module to match the cooling requirements to the system load.  The valves shall be the slow opening type to minimize the sudden change in flow to the previously active modules.  The valves shall have a minimum opening cycle time of not less than 60 seconds between the fully closed and open position.  The valves shall have a minimum close off pressure of not less than 75 psi.

  - Filters:  A 60-mesh industrial grade filter strainer shall be factory installed between the header system and each evaporator inlet.  The strainer shall be serviceable by individual manual isolation valves that permit each strainer to be removed and cleaned without shutting down water flow or power to the entire system and allowing the remaining modules to continue to operate.  In-line strainers that require complete system shutdown for service and isolation are not acceptable.

  - Condenser fan motors:  The condenser fan motors shall have double sealed ball bearings rated for thrust duty with slingers.  The motors shall be rated for high ambient operation with a minimum rating of 60 (C.

  - Condenser Coil:  Aluminum fins mechanically bonded to coppers tubes with integral subcooling circuits. Fin spacing shall not exceed 12 fins per inch.  The coils shall be sized to provide full heat of rejection at jobsite elevation above sea level, at a maximum 25 degree F temperature difference between the condensing temperature and ambient air temperature.  The coils shall be factory tested to a minimum of 600 psig.

  - Flooded Condenser:  Flooded condenser head pressure controls shall be provided for the chiller to operate to -20 F ambient temperatures

  - Refrigerant piping:  Piping shall be Type L seamless copper, and shall have an insulated suction line using closed cell pipe insulation, compressor rotalock service valves, solenoid valves for compressor pumpdown, and Schrader service valves in the suction, discharge, and liquid lines.

  - Water Piping: The water piping shall be Schedule 40 steel, and be insulated using closed cell pipe insulation to prevent condensation. The chiller shall have service valves for the independent isolation of each evaporator, without affecting the water flow to the remaining evaporators. Each chiller module shall connect to the adjacent module using Victaulic rolled groove steel couplings and neoprene gaskets. Any type of module-to-module connection external to the modules is unacceptable.

  - Controls:  The Master chiller module shall incorporate the Master microprocessor controller. The Master microprocessor shall communicate with the remaining Slave microprocessors in each module via a local network communications protocol.  Each microprocessor shall include; operational switches for each compressor; high and low refrigeration pressure switches; low pressure pump down switches; anti-short cycling compressor timers; minimum compressor run timers; and phase monitor to protect against low voltage, phase unbalance, phase loss, and phase reversal conditions. Each chiller module shall incorporate its own flow safety switch for system redundancy and service isolation valve to permit changing of each individual flow switch while the remaining chiller modules are operational. Systems incorporating only one system flow switch are not acceptable.  To facilitate connection to Building Automation System and Remote Monitoring System, the Master controller shall read all analog and fault port values from all Slave module controllers. The Master controller shall be capable of passing values, compatible with BACnet, Modbus or Lonworks protocol, to the Building Automation System.

  - Microprocessor:  The microprocessor shall provide the following minimum functions and alarms:

      - Adjustable fluid temperature set point

      - Multiple stage compressor control, including compressor rotation to provide even compressor usage and wear.

      - High and low fluid temperature alarm set points

      - Water inlet and outlet temperature

      - Suction and discharge refrigeration pressures

      - Compressor run status

      - Current alarm status

      - Demand load

      - Compressor run hours

      - Alarm logging with minimum of previously 100 logged alarms with time and date of each occurrence

      - Remote start stop input

      - Dry contact for general alarm

  - Interface Panel:  A remote operator interface panel shall be provided to allow operator adjustment of user set points, and alarm monitoring.  The remote interface panel shall be installed in the operator’s control room.  The wiring between the chiller and the remote panel shall be provided and installed by the electrical contractor .  The wiring shall be 6-conductor wiring with straight-through connections. The master controller shall be compatible with Ethernet Modbus Gateways and allow for its installation and connection to the electrical service inside the master chiller control panel and to Ethernet connections for Internet-based performance and fault monitoring and alerting.

  - Free Cooling Module

- Frame and Cabinet:  The module shall be constructed on an epoxy coated welded steel frame and enclosed with white painted aluminum panels.  The unit shall be shipped as a separate module and assembled on site.  The module shall be fully factory tested prior to shipment.  Electrical supply shall be via factory provided assembled wiring in flexible, liquid tight conduit and shall be field connected to the load distribution panel on the end chiller module.  This connection shall be performed by the installing contractor.  Bus bar electrical power distribution is unacceptable.

- Fan motors:  The fan motors shall have double sealed ball bearings rated for thrust duty with slingers.  The motors shall be rated for high ambient operation with a minimum rating of 60 (C.

- Coils:  Aluminum fins mechanically bonded to coppers tubes with integral subcooling circuits. Fin spacing shall not exceed 14.  The coils shall be sized to provide partial free cooling in ambients starting at 40F.  The tubes and headers shall be sized for a maximum velocity of no more than 7 ft/sec.

- Three-way Valve:  The module shall include a 3-way, 2-position valve to allow the system fluid to be cooled by free cooling coils when the ambient temperature falls below the ambient temperature set point.  The valve actuator is housed in a Nema 3R weather resistant enclosure.  The module piping shall include isolation valves on all three ports to allow the 3-way valve to be removed from the piping without shutting down the system for service and replacement.  The valve shall be supported from the cabinet framing and not from the system piping.

- Controls:  The module shall include controls to allow the system fluid to be cooled by the free cooling coils upon a drop in ambient temperature below the free-cooling set point.  The set point shall be clearly displayed via a digital LCD display.  This set point is field adjustable.  Systems with analog indication are not acceptable.  The unit shall incorporate field adjustable fan cycling thermostatic controls to cycle the fans in the module to limit the leaving fluid temperature from the module to the acceptable minimum.  These set points are field adjustable.

  - Tank and Pump Module

- General:  The unit shall be shipped as a separate module and assembled on site.  The module shall be fully factory tested prior to shipment.  Electrical supply shall be via factory provided assembled wiring in flexible, liquid tight conduit and shall be field connected to the load distribution panel on the end tank and pump module.  This connection shall be performed by the installing contractor.  Bus bar electrical power distribution is unacceptable

- Frame:  The module shall be constructed on an oven baked, epoxy coated welded steel frame.  The frame shall be of heavy duty, with minimum ¼” thick members.

- Cabinet:  The unit shall be enclosed with white painted aluminum panels.  The cabinet enclosure shall include easily removable access panels for service.  Access panels shall be removable via stainless steel fasteners and retaining clips.  Panels shall not require access via sheet metal screws or protruding threaded fasteners.

- Pumps:  Pumps shall be dual, independent cast iron bronze fitted centrifugal pumps.  Each pump shall have a cast bronze dynamically balanced impeller, stainless steel shaft, carbon ceramic seal with stainless steel nuts and bolts.  The pump motors shall be ODP design and rated for a maximum speed of 3500 rpm.  The pumps shall include inlet and discharge ports for venting and draining.  The pumps shall not require disassembly from the chilled water piping for service access or repair.

- Pump Motors:  The pump motors shall be ODP design and rated for a maximum speed of 3500 rpm.  The motor shall be premium efficient, and shall allow for the pumps to operate on factory provide variable frequency drives.

- Expansion tank: The chiller shall have a factory-mounted expansion tank constructed of epoxy-coated steel with butyl diaphragm.  The tank shall be rated at a minimum of 100 psi and shall be pre-charged at 10 psi.  The tank shall have a readily accessible air charging port, and have an isolation valve in the system piping for service and maintenance.

- Water Piping:  The water piping shall be Schedule 40 steel, and be insulated with closed cell pipe insulation to prevent condensation.  The pump module shall connect to the adjacent module using rolled groove steel couplings and neoprene gaskets.  Any type of module-to-module connection external to the package is unacceptable.

- Controls:  Each pump shall be sized for 100% capacity, and shall include magnetic motor starters and disconnect switches on each pump to allow for service repair while operating the back-up pump.  The pump module shall incorporate microprocessor controller to control all the operations of the pumps. The microprocessor shall communicate with the remaining microprocessors in each module via a local network communications protocol.  The microprocessor shall include operational switches for each pump; leaving water pressure transmitters to display the leaving fluid pressure; and integral pressure differential switch to switch to the backup pump upon loss of pressure of the primary pump.

  - Microprocessor:  The microprocessor shall provide the following minimum functions and alarms:

      - Pump run status

      - Current alarm status

      - Pump run hours

      - Alarm logging with minimum of previously 100 logged alarms with time and date of each occurrence

      - Automatic lead/lag switchover of the pumps once per week

      - Pump discharge pressure

PART 3                EXECUTION

- INSTALLATION

  - Unit shall be installed in accordance with the Manufacturer’s recommendations where shown on the drawings and other provided installation documents.

  - Contractor shall provide an automatic air separator on the system piping.  The air separator shall include the following:

    - The air separator shall be designed to remove system air by means of creating a low velocity vortex to allow air separation and removal via an integral air collector tube.

    - The air separator shall have 4” flanged or grooved connections to match system piping.

    - Air separator shall have an internal strainer with 5/32” diameter perforations designed to direct the accumulated air to the automatic air vent valve.

    - Separator shall have a minimum working pressure of 125 psi, and shall carry the U-1 stamp as required by Section VIII of the ASME Boiler and Pressure Vessel Code.

    - The air separator shall be installed on the return piping to the chiller prior to warm water return connection.

    - Separator shall be manufactured by ITT Bell and Gossett or engineer approved equal.

  - Contractor shall provide an automatic air vent valve on the automatic air separator required in section B.  The automatic air separator shall include the following:

    - The air separator shall be constructed of cast iron and fitted with stainless steel, brass and EPDM.

    - The air separator shall be a high capacity air separator with a minimum air vent opening of not less than 3/8”.

    - The air vent shall be rated for a minimum working pressure of not less than 150 psi.

    - A gooseneck piping connection shall be installed on the air vent opening to prevent rain from entering into the air vent opening and being subjected to freezing in the air vent.

    - The high capacity air vent shall be ITT Bell and Gossett Model 107A or engineer approved equal.

  - Each chiller module is shipped individually for field assembly.  Field assembly of chiller system shall consist of the following minimum steps:

    - Manifold chilled water piping with factory supplied rolled groove connections.  Insulate rolled groove connections after assembly.

    - Connect factory supplied power supply wiring harnesses to the load distribution panel.  Install wires to the proper terminals for proper phasing.  Unit is wired for A, B, C phase right to left in the load distribution panel.  Each wire on the wire harness is identified as to its respective phase.

    - Connect all microprocessors together to form the local communication network.  Wiring must be 20-gauge minimum, single twisted pair, shielded wiring.

  - PIPING FLUSHING PROCEDURE

- Prior to connecting the chiller to the building chilled water loop, the piping shall be flushed with a detergent and hot water (110-130 F) mixture to remove previously accumulated dirt and other organic residue.  In old piping systems with heavy encrustation of inorganic materials, consult a water treatment specialist for proper passivation and/or removal of these contaminants.

- Prior to flushing, install a 30 mesh or finer Y-type strainer or equivalent in the system piping.  During the flushing process, examine and clean the strainer periodically as necessary to remove collected residue.  The flushing process shall take not less than 6 hours or until the strainers, when examined after each flushing, are clean.  Old systems with heavy encrustation shall be flushed for a minimum of 24 hours or until the strainers run clean.  Detergent and acid concentrations shall be used in strict accordance with the respective chemical manufacturer’s instructions.  After flushing with detergent and/or dilute acid concentrations, the system loop shall be purged with clean water for at least one hour to ensure that all residual cleaning chemicals have been flushed out.

3.03    REFRIGERATION SYSTEM START-UP AND TESTING

A.	Factory-supervised start-up and checkout with start-up report shall be provided for each module.  Owner training by factory representative shall be provided.