Specifications for Buderus G334X/132 Series Gas Boilers

- There shall be provided and installed a quantity of 1 G334X Buderus atmospheric gas boilers with an AGA Input rating of  542 MBH each, a Gross Output of 451 MBH each, suitable for firing with Natural Gas or Propane Gas.

- Boilers shall be fabricated with GL-180M high silicone flexible cast iron material.  Boilers shall be of wet leg design with tapered flue ways and sectional cast iron construction with precision grooved and beveled steel push nipples.

- Boilers shall be constructed, tested and labeled in accordance with ASME Section IV and shall bear the ASME stamp. Sections shall be labeled for 58 psig maximum working pressure rating.

- Boilers shall be AGA and CGA certified for firing with Natural and Propane Gas and equipped for operation with 115-volt, 60-cycle, one-phase power. The boilers shall be factory assembled, wired and tested with the jacket and draft diverter packaged separately for ease of entry.

- Boilers shall be furnished with heavy-gauge baked enamel high quality jacket with a full 3" fiberglass insulation on top and all sides, 1½” supply and return connections, 30 PSI pressure relief valve, P&T gauge and boiler drain.

- Boilers shall be furnished with premixed stainless steel factory tested and fired burners, two Honeywell combination gas control valves, and a Honeywell L4006 high limit. The boilers shall consist of two independent gas burner trays to permit step-firing of each boiler module.

- The boilers shall be equipped with a heavy gauge, non-combustible base approved for installation on combustible flooring as well as being approved for closet installation with 2" side clearances.

- The boilers shall have an internal draft diverter for low overall height and easy connection to a chimney connector.

Equipment shall be supplied by an authorized Buderus stocking wholesaler.  Buderus Representative is Klimatrol Environmental Systems (905) 454-1742.