Copyright 2004 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Product MASTERSPEC Section is licensed by ARCOM for limited distribution by Bosch Thermotechnology Corp. (Buderus) ("Licensee").  The license is subject to revocation.  Revisions to the original MASTERSPEC text were made solely by the Licensee.  A clean version (revisions accepted) and an underline-and-strikeout version of this Section, both of which modify the original MASTERSPEC text, are distributed by Licensee to assist in specifying Licensee's products.

Revisions made to the original MASTERSPEC text are provided by the Licensee and are not endorsed by, or representative of the opinions of, ARCOM or The American Institute of Architects (AIA).  A competent design professional should review and edit the document to suit project requirements.  For more information, contact Bosch Thermotechnology Corp. (Buderus), 50 Wentworth Avenue, Londonderry, NH 03053.  Phone (800) 283-3787.  Fax (603) 584-1698.  Website:  www.buderus.net.  Email: commercialsales@bbtna.com.  For information about MASTERSPEC contact ARCOM at (800) 424-5080 or visit www.arcomnet.com.

SECTION 15512 - CAST-IRON BOILERS

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

SUMMARY

This Section includes cast-iron boilers, trim, and accessories for generating hot water with the following configurations and burners:

Adjust list below to suit Project.  Buderus models G315 and G515 are pressure-fired boilers.  Model G615 is a forced-draft gas type boiler.

[Factory] [Field] assembled.

[Sealed-combustion, gas] [Pressure-fired] [Forced-draft, gas] [Oil] [Combination gas and oil] burner.

SUBMITTALS

Product Data:  Include performance data, operating characteristics, furnished specialties, and accessories.

Shop Drawings:  For boilers, boiler trim, and accessories.  Include plans, elevations, sections, details, and attachments to other work.

Retain first subparagraph and associated subparagraphs below if boilers are required to withstand specific design loads and Architect either has delegated design responsibility to Contractor or wants to review structural data as another way to verify boiler's compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

Design calculations and vibration isolation base details, signed and sealed by a qualified professional engineer.

Design Calculations:  Calculate requirements for selecting vibration isolators and seismic restraints and for designing vibration isolation bases.

Vibration Isolation Base Details:  Detail fabrication including anchorages and attachments to structure and to supported equipment.  Include auxiliary motor slides and rails and equipment mounting frames.

Wiring Diagrams:  Power, signal, and control wiring.

Source quality-control test reports.

Field quality-control test reports.

Operation and Maintenance Data:  For boilers, components, and accessories to include in emergency, operation, and maintenance manuals.

Warranty:  Special warranty specified in this Section.

Other Informational Submittals:

Startup service reports specific to burner type.

QUALITY ASSURANCE

Manufacturer Qualifications:  Provides products from ASME-certified factories.

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

ASME Compliance:  Fabricate and label boilers to comply with ASME Boiler and Pressure Vessel Code.

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

ASHRAE/IESNA 90.1 Compliance:  Boilers shall have minimum efficiency according to "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

I=B=R Compliance:  Boilers shall be tested and rated according to HI's "Rating Procedure for Heating Boilers" and "Testing Standard for Commercial Boilers," with I=B=R emblem on a nameplate affixed to boiler.

Retain second option in paragraph below for combination burners.

UL Compliance:  Test boilers for compliance with [UL 726, "Oil-Fired Boiler Assemblies] [UL 726, "Oil-Fired Boiler Assemblies," and UL 795, "Commercial-Industrial Gas Heating Equipment] [UL 795, "Commercial-Industrial Gas Heating Equipment]." Boilers shall be listed and labeled by a testing agency acceptable to authorities having jurisdiction.

COORDINATION

Coordinate size and location of concrete bases.  Cast anchor-bolt inserts into bases.  Concrete, reinforcement, and formwork requirements are specified in Division 3.

WARRANTY

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 1 Section "Product Requirements." See discussion about warranties in "Common Boiler Characteristics" Article in the Evaluations in Division 15 Section "Heating Boilers and Accessories."

Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace controls and heat exchangers of boilers that fail in materials or workmanship within specified warranty period.

Verify available warranties for units and components and insert number below.

Warranty Period for Controls:  Two years from date of Substantial Completion.

Warranty Period for Heat Exchangers:  Five years from date of Substantial Completion.

PRODUCTS

MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations in Division 15 Section "Heating Boilers and Accessories" for cautions about naming manufacturers and products.  See Division 1 Section "Product Requirements."

Basis-of-Design Product:  Subject to compliance with requirements, provide Bosch Thermotechnology Corporation (Buderus); [G315] [G515] [G615], as supplied by a Buderus Stocking Wholesaler, or a comparable product by one of the following:

Viessmann Manufacturing Co. Inc.

Weil-McLain; a United Dominion Company.

<Insert manufacturer's name.>

MANUFACTURED UNITS

Description:  Factory fabricated and [field ]assembled.

Retain one of two subparagraphs below.  Retain first for factory-assembled boilers and second for field-assembled boilers.

Cast-iron sections shall be sealed pressure tight and held together with steel push nipples; including insulated jacket and flue-gas vent connection.

Ship cast-iron sections disassembled with all materials and equipment, including seals, push nipples, spring tension rods, and insulated jacket and flue-gas vent connection for field assembly.

Cast-Iron Section Design:

Configuration:  Wet [base] [back].

Number of Passes:  Three.

Sectional Joints:  High-temperature sealant to seal flue-gas passages not in contact with heating medium, held together with steel push nipples.

Drain and blowdown tappings.

Return injection tube to distribute water flow to each section based on flame profile in the combustion chamber.

Crown inspection tappings with brass plugs.

Combustion Chamber:  Equipped with a single flame observation port.

Casing:

Jacket:  [Galvanized ]sheet metal, with snap-in or interlocking closures and electrostatic powder-coated protective finish.

Insulation thickness on models G315 and G515 is 3-1/2-inches.  Insulation on model G615 is 4-inches thick.

Insulation:  Minimum [3-1/2-inch- (89-mm-)] [4-inch- (102-mm-)] thick, glass fiber insulation surrounding the heat exchanger.

Feature in first subparagraph below is unique for some boiler manufacturers.

Combustion Chamber Access:  Full-sized door, hinged left or right.

Access:  For cleaning between cast-iron sections from the front of the boiler.

Draft Hood:  Flue canopy and rear flue connection shall be constructed of cast iron.

Retain one of five "Burner" articles below.

BURNER

Retain this Article for forced-draft, sealed combustion, or pressure-fired gas burners.

Burner:  Welded construction with [multivane] [flat plate], [steel] [stainless-steel], flame-retention diffuser for [natural] [propane] gas.

Blower:  [Forward-curved] [Reverse incline] centrifugal fan integral to burner, directly driven by motor; with adjustable, [single-blade] [dual-blade] [butterfly] damper assembly and locking quadrant to set air-fuel ratio.

Burner Control:  [Linkage-driven] [Linkage-less] burner controls.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

Motors:  Comply with requirements specified in Division 15 Section "Motors."

Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In first paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

Gas Train:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL] [ULC].

Pilot:  [Intermittent] [Interrupted] [Direct]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with [cadmium sulfide] [UV scanner] [flame rod] flame-safety control.

Retain paragraph and subparagraph below to decrease oxides of nitrogen emissions.  Not all manufacturers can comply with options listed below.  Edit to suit Project.

Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

Maximum Oxides of Nitrogen Emissions:  [20] [30] <Insert amount> ppm.

Low Nitrogen Oxide:  Burner equipped for low nitrogen oxides with a premix head.

Maximum oxides of nitrogen emissions:  [20] [30] <Insert amount> ppm.

BURNER

Retain this Article for oil burners.

Burner:  Welded construction with [multivane] [flat plate], [steel] [stainless-steel], flame-retention diffuser for fuel oil.

Blower:  [Forward-curved] [Reverse-incline] centrifugal fan integral to burner, directly driven by motor; with adjustable, [single-blade] [dual-blade] [butterfly] damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

Motors:  Comply with requirements specified in Division 15 Section "Motors."

Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In first paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

Oil Supply:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL] [ULC].

Oil pump may be remotely mounted and shipped separately.  Edit performance parameters in first subparagraph below to suit Project.

Oil Pump:  Two-stage, gear-type oil pump[ integral to and directly driven by blower] [burner-mounted, independently driven] shall be capable of producing 300-psig (2070-kPa) discharge pressure and 13-inch Hg (43.9-kPa) vacuum.

Oil Piping Specialties:

Suction-line, manual, gate valve.

Removable-mesh oil strainer.

0- to 30-inch Hg (0- to 101.3-kPa) vacuum; 0- to 30-psig (0- to 207-kPa) vacuum-pressure gage.

0- to 300-psig (0- to 2070-kPa) oil-nozzle pressure gage.

Nozzle-line, solenoid-safety-shutoff oil valve.

Pilot:  [Intermittent] [Interrupted] [Direct]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff solenoid using [cadmium sulfide] [UV scanner] [flame rod] flame-safety control.

BURNER

Retain this Article for combination gas and oil burners.

Burner:  Welded construction with [multivane] [flat plate], [steel] [stainless-steel], flame-retention diffuser for fuel oil and [natural] [propane] gas.

Blower:  [Forward-curved] [Reverse incline] centrifugal fan integral to burner, directly driven by motor; with adjustable, [single-blade] [dual-blade] [butterfly] damper assembly and locking quadrant to set air-fuel ratio.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 15 Section "Motors." If different characteristics are required, add subparagraphs below to suit Project.

Motors:  Comply with requirements specified in Division 15 Section "Motors."

Motor Sizes:  Minimum size as indicated.  If not indicated, large enough so driven load will not require motor to operate in service factor range above 1.0.

In paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

Oil Supply:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL] [ULC].

Oil pump may be remotely mounted and shipped separately.  Edit performance parameters in first subparagraph below to suit Project.

Oil Pump:  Two-stage, gear-type oil pump[ integral to and directly driven by blower] [burner-mounted, independently driven] shall be capable of producing 300-psig (2070-kPa) discharge pressure and 13-inch Hg (43.9-kPa) vacuum.

Oil Piping Specialties:

Suction-line, manual, gate valve.

Removable-mesh oil strainer.

0- to 30-inch Hg (0- to 101.3-kPa) vacuum; 0- to 30-psig (0- to 207-kPa) vacuum-pressure gage.

0- to 300-psig (0- to 2070-kPa) oil-nozzle pressure gage.

Nozzle-line, solenoid-safety-shutoff oil valve.

In first paragraph below, retain any of three control sequences with any of four safety requirements.  Availability of three control sequences listed depends on boiler capacity.  Consult boiler manufacturer.

Gas Train:  Control devices and [modulating] [on-off] [low-high-low] control sequence shall comply with requirements in [ASME CSD-1] [FMG] [IRI] [UL] [ULC].

Gas Pilot:  [Intermittent] [Interrupted] [Direct]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff with [cadmium sulfide] [UV scanner] [flame rod] flame-safety control.

Oil Pilot:  [Intermittent] [Interrupted] [Direct]-electric-spark pilot ignition with 100 percent main-valve and pilot-safety shutoff solenoid with [cadmium sulfide] [UV scanner] [flame rod] flame-safety control.

Retain paragraph and subparagraph below to decrease oxides of nitrogen emissions.  Not all manufacturers can comply with options listed below.  Edit to suit Project.

Flue-Gas Recirculation:  Burner connections shall be equipped for recirculating flue gas.

Maximum Oxides of Nitrogen Emissions:  [20] [30] <Insert amount> ppm.

Retain one of two "Trim" articles below.

TRIM

Retain this Article for hot-water boilers.

Include devices sized to comply with ANSI B31.9, "Building Services Piping."

Retain option in first paragraph below if using modulating or low-high-low firing sequence.

Aquastat Controllers:  Operating[, firing rate,] and high limit.

Safety Relief Valve:  ASME rated.

Pressure and Temperature Gage:  Minimum 3-1/2-inch- (89-mm-) diameter, combination water-pressure and -temperature gage.  Gages shall have operating-pressure and -temperature ranges so normal operating range is about 50 percent of full range.

Drain Valve:  Minimum NPS 3/4 (DN 20) hose-end gate valve.

CONTROLS

Retain paragraph below if controls are specified in Division 15 Section "HVAC Instrumentation and Controls."

Refer to Division 15 Section "HVAC Instrumentation and Controls."

Delete paragraph above and retain first two paragraphs and associated subparagraphs below if controls are components of boilers.  Coordinate with Division 15 Section "HVAC Instrumentation and Controls."

Boiler operating controls shall include the following devices and features:

Control transformer.

Set-Point Adjust:  Set points shall be adjustable.

Retain one of two subparagraphs below for operating control sequences.  Retain one of first two subparagraphs for hot-water boilers; or third, for steam boilers.

Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to maintain space temperature in response to thermostat with heat anticipator located in heated space.

Sequence of Operation:  Electric, factory-fabricated and field-installed panel to control burner firing rate to reset supply-water temperature inversely with outside-air temperature.  At [14 deg F (minus 10 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [168 deg F (76 deg C)] <Insert temperature>; at [50 deg F (10 deg C)] <Insert temperature> outside-air temperature, set supply-water temperature at [113 deg F (45 deg C)] <Insert temperature>.

Retain subparagraph below with any of three "Sequence of Operation" subparagraphs above.

Include automatic, alternating-firing sequence for multiple boilers by hours run and load limit, in either parallel or series operation.

Burner Operating Controls:  To maintain safe operating conditions, burner safety controls limit burner operation.

In subparagraph below, retain "temperature" option for hot-water boiler and "pressure" option for steam boiler.

High Cutoff:  Manual reset stops burner if operating conditions rise above maximum boiler design temperature.

In subparagraph below, retain first option for hot-water boilers and second option for steam boilers.

Low-Water Cutoff Switch:  Electronic probe shall prevent burner operation on low water.  Cutoff switch shall be manual-reset type.

First two subparagraphs below apply to atmospheric burners.  Some boilers may be equipped with only one of two switches below.  Verify availability with boiler manufacturer.

Blocked Vent Safety Switch:  Manual-reset switch field-installed on breeching.

Audible Alarm Output:  Factory mounted on control panel.

Flue Gas Temperature Sensor:  Factory-installed control panel connection and factory-supplied field-installed sensor on breeching; shall shut down boiler at <Insert temperature>.

Retain paragraph and subparagraphs below if boiler controls interface with building automation system.

Building Automation System Interface:  Factory install hardware and software to enable building automation system to monitor, control, and display boiler status and alarms.

Retain subparagraph and associated subparagraphs below if interface with building automation system is through hardwired points and minimal interface is required.  If extensive interface is required, delete below and retain second subparagraph below.

Hardwired Points:

Monitoring:  On/off status, [common trouble alarm] [low water level alarm] <Insert monitoring>.

Control:  On/off operation, [hot water supply temperature set-point adjustment] [steam pressure adjustment] <Insert control>.

Retain subparagraph below if extensive interface with building automation system is required and is beyond that than can be provided by hardwired points.  Requirement may exclude some manufacturers listed.  Eschelon Company provides "LonWorks" building management software.  Buderus offers a compatible building automation gateway system for its boilers called "Buderus Logomatic LON-Gateway."

A ["Buderus Logomatic LON-Gateway"] communication interface with building automation system shall enable building automation system operator to remotely control and monitor the boiler from an operator workstation.  Control features available, and monitoring points displayed, locally at boiler control panel shall be available through building automation system.

ELECTRICAL POWER

Retain one of two paragraphs and associated subparagraphs in this Article.  Retain first if single-point field power connection is not applicable; retain second if single-point field power connection is applicable.

Controllers, Electrical Devices, and Wiring:  Electrical devices and connections are specified in Division 16 Sections.

CAPACITIES AND CHARACTERISTICS

If Project has more than one type or configuration of boiler, delete this Article and schedule boilers on Drawings.

Heating Medium:  Hot water.

Retain one of first two paragraphs below.  Retain first for hot-water boilers and second for steam boilers.  For steam boilers, limit steam pressure to 15 psig (104 kPa) or less.

Design Water Pressure Rating:  87 psig (600 kPa).

Safety Relief Valve Setting:  <Insert psig (kPa).>

Retain three paragraphs below for hot-water boilers.

Leaving-Water Temperature:

For model G315 boilers using Buderus controls, no specified leaving-water temperature is required.  Retain first two paragraphs below only if Buderus controls will not be required with this boiler.

On/Off Burner Minimum Supply Temperature: 131 deg F (55 deg C).

Modulating or Low/High/Low Burner Minimum Supply Temperature: 149 deg F (65 deg C).

For model G515 and G615 boilers using Buderus controls, no specified leaving-water temperature is required.  Retain two paragraphs below only if Buderus controls will not be required with these boilers.

Oil Burner Minimum Supply Temperature: 122 deg F (50 deg C).

Gas Burner Minimum Supply Temperature: 140 deg F (60 deg C).

Buderus boilers have no minimum flow rate requirement.

Design Water Flow Rate:  <Insert gpm (L/s).>

Design Pressure Drop:  <Insert psig (kPa).>

Retain one of first two paragraphs below.  If applying for LEED certification, efficiency must be equal to or greater than minimum efficiency required by ASHRAE/IESNA 90.1-2004, Table 6.8.1F, "Gas and Oil Fired Boilers - Minimum Efficiency Requirements."

Minimum Thermal Efficiency:  <Insert value> percent.

Minimum Combustion Efficiency:  <Insert value> percent.

Number of Passes:  Three.

Retain one of first three paragraphs below.  Retain one of first three input rating methods for gas.

I=B=R Input:  <Insert MBh (kW).>

Consider actual Btu content of fuel source if retaining paragraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

Gas Input:  <Insert cfh (mL/s).>

Consider actual Btu content of fuel source if retaining paragraph below.  Contact fuel supplier and boiler manufacturers to determine impact.  Add text indicating Btu content of fuel if applicable.

Oil Input:  <Insert gph (mL/s).>

Retain one of two paragraphs below for rating methods.

Net I=B=R Output Capacity:  <Insert MBh (kW).>

Gross I=B=R Output Capacity:  <Insert MBh (kW).>

Consider impact of site altitude on fan and motor.

Blower:

Motor Horsepower:  <Insert value.>

RPM:  <Insert value.>

Electrical Characteristics:

Volts:  [115] [208] [230] [460] <Insert value> V.

Phase:  [Single] [Three].

Hertz:  [50] [60].

Full-Load Amperes:  <Insert value.>

Minimum Circuit Ampacity:  <Insert value.>

Maximum Overcurrent Protection:  <Insert amperage.>

SOURCE QUALITY CONTROL

Retain this Article for factory-assembled boilers.  Factory tests are an additional cost item.

Test and inspect factory-assembled boilers, before shipping, according to ASME Boiler and Pressure Vessel Code.

EXECUTION

EXAMINATION

Before boiler installation, examine roughing-in for concrete equipment bases, anchor-bolt sizes and locations, and piping and electrical connections to verify actual locations, sizes, and other conditions affecting boiler performance, maintenance, and operations.

Final boiler locations indicated on Drawings are approximate.  Determine exact locations before roughing-in for piping and electrical connections.

Examine mechanical spaces for suitable conditions where boilers will be installed.

Proceed with installation only after unsatisfactory conditions have been corrected.

BOILER INSTALLATION

Install boilers level on concrete base.  Concrete base is specified in Division 15 Section "Basic Mechanical Materials and Methods," and concrete materials and installation requirements are specified in Division 3.

Coordinate selection of device and deflection in first paragraph below with Division 15 Section "Mechanical Vibration and Seismic Controls."

Vibration Isolation:  Elastomeric [isolator pads] [mounts] with a minimum static deflection of [0.25 inch (6.35 mm)] <Insert deflection>.  Vibration isolation devices and installation requirements are specified in Division 15 Section "Mechanical Vibration and Seismic Controls."

Install gas-fired boilers according to NFPA 54.

Retain paragraph above for gas-fired boilers and paragraph below for oil-fired boilers, or both for combination gas- and oil-fired boilers.

Install oil-fired boilers according to NFPA 31.

Delete first paragraph below if boiler is delivered fully assembled.

Assemble boiler sections in sequence and seal between each section.

Assemble and install boiler trim.

Install electrical devices furnished with boiler but not specified to be factory mounted.

Install control wiring to field-mounted electrical devices.

CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Piping installation requirements are specified in other Division 15 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

Install piping adjacent to boiler to allow service and maintenance.

Connect gas piping to boiler gas-train inlet with union.  Piping shall be at least full size of gas train connection.  Provide a reducer if required.

Retain paragraph above for gas-fired boilers and first paragraph below for oil-fired boilers, or both for combination gas- and oil-fired boilers.

Connect oil piping full size to burner inlet with shutoff valve and union.

Connect hot-water piping to supply- and return-boiler tappings with shutoff valve and union or flange at each connection.

Install piping from safety relief valves to nearest floor drain.

Retain paragraph above for hot-water boilers.  Delete if safety valves are specified in Division 15 Section "Steam and Condensate Piping" or "Hydronic Piping."

Install piping from equipment drain connection to nearest floor drain.  Piping shall be at least full size of connection.  Provide an isolation valve if required.

Connect breeching full size to boiler outlet.  Comply with requirements in Division 15 Section "Breechings, Chimneys, and Stacks" for venting materials.

Install flue-gas recirculation duct from vent to burner.  Comply with requirements in Division 15 Section "Breechings, Chimneys, and Stacks" for recirculation duct materials.

Ground equipment according to Division 16 Section "Grounding and Bonding."

Connect wiring according to Division 16 Section "Conductors and Cables."

FIELD QUALITY CONTROL

Perform tests and inspections and prepare test reports.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with inspections, tests, and adjustments.  Factory-authorized service representative visits are an additional cost item.

Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect components, assemblies, and equipment installations, including connections, and to assist in testing.

Tests and Inspections:

Perform installation and startup checks according to manufacturer's written instructions.

Leak Test:  Hydrostatic test.  Repair leaks and retest until no leaks exist.

Operational Test:  Start units to confirm proper motor rotation and unit operation.  Adjust air-fuel ratio and combustion.

Test and adjust controls and safeties.  Replace damaged and malfunctioning controls and equipment.

Burner Test:  Adjust burner to eliminate excess oxygen, carbon dioxide, oxides of nitrogen emissions, and carbon monoxide in flue gas and to achieve combustion efficiency.

Check and adjust initial operating set points and high- and low-limit safety set points of fuel supply, water level and [water temperature] [steam pressure].

Set field-adjustable switches and circuit-breaker trip ranges as indicated.

Remove and replace malfunctioning units and retest as specified above.

Retain subparagraph below to require a factory-authorized service representative to assist Contractor with  adjustments.  Factory-authorized service representative visits are an additional cost item.

Occupancy Adjustments:  When requested within [12 months of date of Substantial Completion] <Insert time period>, provide on-site assistance in adjusting system to suit actual occupied conditions.  Provide up to [two] <Insert number> visits to Project during other than normal occupancy hours for this purpose.

Retain paragraph and subparagraphs below if performance tests are required.  Performance verification based on field tests is not typically required because of the associated cost.  Consult Owner.  Factory-authorized service representative visits are an additional cost item.

Performance Tests:

Engage a factory-authorized service representative to inspect component assemblies and equipment installations, including connections, and to conduct performance testing.

Boilers shall comply with performance requirements indicated, as determined by field performance tests.  Adjust, modify, or replace equipment to comply.

Perform field performance tests to determine capacity and efficiency of boilers.

For dual-fuel boilers, perform tests for each fuel.

Test for full capacity.

Test for boiler efficiency at [low fire 20, 40, 60, 80, 100, 80, 60, 40, and 20] <Insert range> percent of full capacity.  Determine efficiency at each test point.

Repeat tests until results comply with requirements indicated.

Provide analysis equipment required to determine performance.

Provide temporary equipment and system modifications necessary to dissipate the heat produced during tests if building systems are not adequate.

Notify Architect in advance of test dates.

Document test results in a report and submit to Architect.

Factory-authorized service representative visits are an additional cost item.

DEMONSTRATION

[Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain boilers.[  Video training sessions.] Refer to Division 1 Section "Demonstration and Training."

END OF SECTION 15512