Suggested Long-Form Specification: Hydronic Snow and Ice Melting Systems

# General

# Work Included

# Regulatory Requirements

# References

# Submittals

# Delivery, Storage and Handling

# Warranty

# Products

# Piping

# Fittings

# Manifolds

# Controls

# Accessories

# InsulPex Buried Mains

# System Performance

# Execution

# Preparation

# Installation

# Field Quality Control

# General

# Work Included

# Description:  Furnish and install a REHAU Snow and Ice Melting (SIM) system as supplied by KLIMATROL Environmental Systems Ltd.  (905) 454-1742.  Systems shall be complete with REHAU piping, distribution manifold(s) , pipe to manifold compression nut fittings, manufacturer-approved cold-expansion compression-sleeve pipe repair couplings (if required) and non-metallic pipe fasteners. Snow Melt controls and associated snow detector sensors, mixing control valve, pumps and  installation specialties, site supervision and field engineering as required for complete and proper function of the system shall be provided by Klimatrol. Alternate systems shall be submitted with material cost savings.

# Regulatory Requirements

# Cross-linked polyethylene (PEXa) pipe shall be manufactured by the high-pressure peroxide (Engel) method with a minimum degree of cross-linking of 80%, and conform to ASTM F 876, F 877 and CSA B 137.5.  Fittings shall conform to ASTM F 877, F 2080 and CSA B 137.5.  Pipe oxygen diffusion barrier shall conform to DIN 4726.

# References

# ASTM F 876: Standard Specification for Cross-linked Polyethylene (PEX) Pipe

# ASTM F 877: Cross-linked Polyethylene (PEX) Plastic Hot- and Cold-Water Distribution Systems

# ASTM F 2080: Standard Specification for Cold-Expansion Fittings with Metal Compression-Sleeves for use with Cross-linked Polyethylene (PEX) Pipe

# CSA B 137.5: Cross-linked Polyethylene (PEX) Tubing Systems for Pressure Applications

# DIN 4726: German Standard for Plastic Piping Used in Warm Water Floor Heating Systems

# Submittals

# Provide submittals and shop drawings in accordance with the General Requirements and as specified herein.  Submit shop drawings indicating schematic layout of system, including equipment, critical dimensions and piping/slab penetration details as well as details for protecting exposed PEX piping.

# Submit manufacturer's technical installation instructions.

# Submit independent certification results for the piping systems from a recognized testing laboratory.

# Submit computer-generated SIM system design indicating pipe sizing and panel performance at pipe spacing and water temperatures selected.  SIM design calculations to be performed on pipe manufacturer’s software.

# Submit catalog data on all equipment, fittings, fasteners and associated items necessary for the installation of the piping and manifolds.

# Submit installers resume of successful snow ice melting or radiant floor heating installations and manufacturer’s training certification.

# Delivery, Storage and Handling

# Deliver and store piping and equipment in shipping containers with labeling in place.  Pipe to be kept in original shipping boxes until required for installation.  Do not expose pipe to ultraviolet (sun) light for more than 90 days.

# Protect piping and manifolds from entry of contaminating materials by installing suitable plugs in all open pipe ends until installation.  Where possible, connect pipes to assembled manifolds to eliminate possibility of contaminants.

# Piping shall not be dragged across the ground or concrete surfaces, and shall be stored on a flat surface with no sharp edges.

# Pipe shall be protected from oil, grease, paint, direct sunlight and other elements as recommended by manufacturer.

# Warranty

# The Snow and Ice Melt pipe manufacturer shall warrant the cross-linked polyethylene piping to be free from defects in material and workmanship for a period of twenty-five (25) years.  Everloc couplings, if used, shall be warranted for 25 years from any defects. The design shall be approved either by submittal or stamped by a registered engineer as being complete and accurate.

# All manifolds and controls shall be warranted for 18 months and/or two seasons of operation.

# Products

# Piping

# Material: All snow & ice melt system piping shall be high density cross-linked polyethylene manufactured using the peroxide method of cross-linking (PEXa) and with an approved cell classification in accordance with ASTM D3350.  Pipe shall conform with ASTM F876 and CSA B137.5, and be certified by CSA or equivalent testing organization.

# Temperature and Pressure Ratings: Piping shall be rated for 100 PSIG gauge pressure at 180oF temperature (690 kPa @ 82°C) continuous, and 80 PSIG gauge pressure at 200oF temperature (550 kPa @ 93°C) continuous.

# Oxygen Diffusion Barrier: Piping shall have a co-extruded oxygen diffusion barrier capable of limiting oxygen diffusion through the pipe to less than 0.10 mg/l/day at 104oF (40°C) water temperature, in accordance with DIN 4726. Oxygen Diffusion Barrier not required when ferrous (iron or steel) components do not share the same system fluid as the cross-linked polyethylene pipe, such as when separated by a heat exchange device.

# Bend Radius: The minimum bend radius for cold bending of the pipe shall be not less than five (5) times the outside diameter.  Bends with a radius less than this shall require the use of a bending template as supplied by the pipe manufacturer, and/or hot air.

# Fittings

# Fittings shall be manufactured of dezincification-resistant brass and shall be supplied by the piping manufacturer as part of a proven cataloged system.   Manifold fittings to be compression nut style with split compression ring.

# Fittings shall be certified to ASTM F 877, F 2080 and CSA B 137.5 as part of the manufacturer’s PEX piping system.  Pipe couplings embedded within the thermal mass shall be EVERLOC® cold-expansion compression-sleeve fittings.

# Manifolds

# Material:  Industrial sized distribution manifolds shall be manufactured and be supplied by the piping manufacturer as a proven cataloged part of the manufacturer's system.

# Snow Ice Melting (SIM) Detector And Melting Controls

# Automatic SIM Detector and Melting Controls: SIM control shall use low-voltage devices to monitor outdoor ambient, slab, fluid supply and/or return temperatures, as well as an automatic snow and ice detector to detect moisture in the SIM zone.  SIM control shall be capable of maintaining a set temperature in a SIM slab or thermal mass, with two adjustable settings for Idle and Melting mode.  Connection to output devices shall be as per the recommended installation of the SIM control, as part of a proven cataloged system.

2.4.2	The snow/ice melting control and detector shall be capable of automatically operating the system including:

1)	Melting at set point (34 - 44 Deg.F.) when precipitation is detected.

2)	Idling at set point (22 Deg.F.) when snow or ice is not detected

- Shutting down the system on outdoor temperature rise above set point (34 - 44 Deg.F.)

- Shutting down system when outdoor temperature drops below set point (-5 – 10 Deg.F.)

- Modulating the temperature input into slab to maintain a maximum temperature differential setting. (25 – 50 Deg.F.)

- 24V output to modulating mixing valve

- Remote enable/disable switch

2.4.3	There shall be one control system for each system.

2.4.4	KLIMATROL Environmental Systems Ltd. shall assist in the commissioning of the control system and snow melting system.

2.5	Accessories

2.5.1.	Utilize manufacturer’s system installation accessories including: nylon cable binders, pipe sleeves, protective sleeving, pipe cutters, pipe uncoilers and other installation tools and aids and pipe ties.

2.7		Performance

Area 1: 	            	Front entry and Wheelchair Ramp (173 sq.m.)

Heat Output Capacity	281,160 Btuh

Flow Requirement 		24 USGPM (25 Deg.F. T. Diff.)

Estimated Headloss		31 Ft. (includes for tubing and manifold only)

Construction			Concrete topping

Tube Spacing:		6” between pipes

Type Tubing:	 REHAU  “CSA” RAUPEX PEX “a” x-linked                                                 polyethylene tubing with Oxygen Diffusion Barrier

No. of Manifolds		One (per drawing)

Design Mean Water Temp.130 Deg.F.

# Execution

# Preparation

# General Contractor shall provide 1 Inch Styrafoam insulation to be installed under the SIM system to prevent downward heat loss and to increase SIM system response time.

# Concrete Slab

# Reinforcing wire mesh or rebar, if required by structural design, must be flat and level, with all sharp ends pointing down.  Finished grade of the thermal mass must be a minimum of 3/4" (19 mm) above the top of PEX heating pipes and not more than 65mm above the top of PEX heating pipes.

    - On Structural Concrete: Concrete surface must be clean and free from all construction debris that could potentially damage the pipe. Insulation, if used, to be installed above existing surface. Finished grade of the thermal mass overpour must be a minimum of 3/4” (19 mm) above the top of PEX heating pipes.

    - Interlocking stone – install piping attached to a wire mesh grid and cover with 2” of screenings and gentlt tamp. Then install interlocking stone or pavers.

    - Preparation of Space for Manifold Installation: Review drawings and/or design to determine proper locations for manifold.  Manifold should be installed in a secure location within a steel manifold cabinet or behind a steel access panel.  If mounted outdoors or in an unheated indoor environment, manifold and pipe tails should be insulated against heat loss. Check cabinet specifications to determine the width of the wall cabinet (if required) and required wall opening dimensions.  Mount the manifold cabinet allowing space for the screed to fill up the front of the pipe opening.  If a cabinet is not used, prepare a suitable cavity for the manifold, with a secure mounting plate that will place the manifold at least 30 inches (75 cm) above floor level.  Manifold must be installed in an area that will allow easy access for supply/return piping as well as future access for maintenance.

  - Installation

    - Install in accordance with manufacturer's published installation manual and/or published guidelines.

    - Mount manifolds in the locations previously prepared or in previously installed cabinets, if used.  Manifolds should be mounted as level as possible.

    - Route piping in orderly manner, according to layout and spacing shown in approved submittal drawings.  All notes on drawings shall be followed.

    - At connections and fittings, use a plastic pipe cutter to ensure square and clean cuts, and join pipes immediately or cap ends of pipe to seal from contaminants. Where fittings are installed within the thermal mass, they shall be wrapped in chloride-free tape or sealed within a heat-shrink Material approved by the manufacturer.

    - Pipe should be dispensed using a suitable uncoiling device.  Remove all twists prior to securing pipe.  Pipe must lie flat on an even plane.  Finished grade of a thermal mass must be a minimum of 3/4” (19 mm) above the top of PEX heating pipes.  Fasten piping at no more than 3 feet (90 cm) intervals, being careful not to twist the pipe.  In thin concrete slabs, it may be necessary to secure piping every 2 feet (60-cm).  Use only fasteners supplied or approved by the manufacturer of the PEX pipe.

    - Piping that must pass through expansion joints shall be covered in protective polyethylene convoluted sleeving (flexible conduit) extending 15 inches (38 cm) on each side of the joint.  Sleeving must be secured on pipe to prevent movement during installation of thermal mass.

    - Where piping exits the thermal mass, a protective conduit shall be placed around the pipe, with the conduit extending a minimum of 6 inches (15 cm) into the floor and exiting by a minimum of 6 inches.  For penetrations at manifolds, use rigid PVC bend guides secured in place to prevent movement.

    - At the time of installation of each circuit of pipe, connect the pipe to the correct manifold outlet and record pipe length for balancing.  If manifold is not installed, cap the end of the pipe and label the pipe's circuit numbers along with S for supply and R for return.  Connect pipes to manifold as soon as possible and record circuit lengths.  All circuits shall be labeled to indicate circuit length and serviced area.

    - The SIM system should not be put into operation until poured concrete thermal mass has cured a minimum of 28 days, unless otherwise specified and approved by thermal mass supplier.  If it is necessary to operate the SIM system to prevent freezing, a maximum flow temperature of 72o F (22°C) must not be exceeded while the thermal mass is curing.  After curing, gradually increase the flow temperature by no more than 10oF (6°C) each day until system reaches the required operating temperature.

Contractor shall be responsible for provision of

- Wire mesh or rebar to secure tubing and any insulations to be provided by the general contractor

- styrafoam insulation beneath slab or setting bed.

- Labour to install Radiant Floor Heating system

- Water, glycol and any chemical solutions.

- Field coordination of the pressure test equipment. (It is recommended to use the REHAU hydraulic pressure test unit available through Klimatrol to conduct pressure tests.)

- Supervision of concrete pours to instruct concrete installers on maintenance of pipe integrity and position of pipe in slab during concrete installation.

- Installation of control valves, pumps, supply and return piping, all valves and fittings.

  - Field Quality Control

    - Filling, Testing & Balancing: Tests of hydronic heating systems shall comply with local codes, and, where required, shall be witnessed by the building official. (Reference BOCA, ICBO, SBCCI or the acceptable code body for the jurisdiction).

      - Pressure gauges used must show pressure increments of 1 PSIG and should be located at or near the lowest points in the distribution system.

    - Air Test: Charge the completed, yet unconcealed pipes with air.  Do not exceed 150 PSIG.  Use liquid gas detector or soap solution to check for leakage at manifold connections.

      - Perform a preliminary pressure test pressurizing the system to the greater of 1.5 times the maximum operating pressure or 100 psi for 30 minutes.  As the piping expands, restore pressure, first at 10 minutes into the test and again at 20 minutes.  At the end of the 30 minute preliminary test, pressure must not fall by more than 5 PSIG from the maximum, and there shall be no leakage.

      - After performing the preliminary test, perform the main pressure test immediately.  The main pressure test shall last 2 hours.  The test pressure should be restored and must not fall more than 3 PSIG after 2 hours.  No leakage should be detected.

      - Pressure shall be maintained and monitored during installation of the thermal mass.  If any leak is detected during installation of thermal mass, the leak must be found immediately and the area cleared for repair using manufacturer approved repair coupling.  Retest before covering repair.